## Contents
sheet | section | columns | rows
01 Headline figures | Headline figures | measure, value | 16
02 Products by manufacturer | Products by manufacturer | manufacturer, products, share, primary, companion, with load, load empty, element types | 6
03 Products by product line | Products by product line | product line, manufacturer, products, share, roles, element types | 13
04 Products by element type | Products by element type | element type, products, share of catalogue, primary, companion, with OD window, with nominal diameter, with load | 8
05 Manufacturer by element type | Manufacturer by element type | manufacturer, pipe, duct_round, duct_rectangular, duct_flex, radiator, threaded_rod, channel, ceiling_anchor, products | 7
06 Products by role | Products by role | role, products, share, cumulative share | 2
07 Field completeness | Field completeness | field, filled, empty, filled share | 11
08 Connection threads | Connection threads | thread, products, share of catalogue | 3
09 Connection threads | Connection threads | thread combination, role, products, share of catalogue | 7
10 Pipe-clamp windows | Pipe-clamp windows | id, manufacturer, article, min mm, max mm, span mm, threads, load kN | 14
11 Descriptive statistics of pi | Descriptive statistics of pipe-clamp windows | series, n, sum, min, max, range, mean, median, sample stdev, q1, q3 | 4
12 Overlapping pipe-clamp windo | Overlapping pipe-clamp windows | article A, article B, overlap min mm, overlap max mm, overlap width mm | 17
13 Merged clamp coverage and ho | Merged clamp coverage and holes | covered from mm, covered to mm, width mm | 4
14 Merged clamp coverage and ho | Merged clamp coverage and holes | hole after mm, hole before mm, width mm | 3
15 Descriptive statistics of in | Descriptive statistics of integer clamp depth | series, n, sum, min, max, range, mean, median, sample stdev, q1, q3 | 1
16 Descriptive statistics of in | Descriptive statistics of integer clamp depth | clamps at that mm, integer mm count, share of the scanned mm, cumulative share | 5
17 Descriptive statistics of in | Descriptive statistics of integer clamp depth | uncovered integers from mm, uncovered integers to mm, count of integers | 2
18 Clamp depth at each integer | Clamp depth at each integer millimetre | mm, matching clamps, product ids | 109
19 Published loads | Published loads | id, manufacturer, element type, value, unit, kN, kind | 13
20 Published loads | Published loads | series, n, sum, min, max, range, mean, median, sample stdev, q1, q3 | 6
21 Published loads | Published loads | id, manufacturer, element type, article | 10
22 Anchors stored on products | Anchors stored on products | id, manufacturer, anchor type, thread, substrate, included fixings, load kN | 3
23 Anchors stored on products | Anchors stored on products | substrate, products, share of anchored products, cumulative share | 2
24 Guidance records | Guidance records | id, applies to, rows, rows flagged table_row, sources, note characters | 3
25 Guidance rows copper-tube-sp | Guidance rows: copper-tube-spacing-din1988-2-as-cited | outer_diameter_mm, horizontal_m, form | 12
26 Guidance rows copper-tube-sp | Guidance rows: copper-tube-spacing-din1988-2-as-cited | series, n, sum, min, max, range, mean, median, sample stdev, q1, q3 | 1
27 Guidance rows copper-tube-sp | Guidance rows: copper-tube-spacing-din1988-2-as-cited | series, n, sum, min, max, range, mean, median, sample stdev, q1, q3 | 1
28 Guidance rows lindab-duct-su | Guidance rows: lindab-duct-suspension-spacing | shape, diameter_mm, horizontal_m, table_row, conditions, width_mm, height_mm | 6
29 Guidance rows lindab-duct-su | Guidance rows: lindab-duct-suspension-spacing | series, n, sum, min, max, range, mean, median, sample stdev, q1, q3 | 1
30 Inventory by model | Inventory by model | model, file, schema, elements, share of elements, groups, recorded length m, elements matched, elements with assumption, elements unmatched, element matched share, element unmatched share, groups matched, groups with assumption, groups unmatched | 3
31 Elements by kind | Elements by kind | kind, elements, share of elements, cumulative share | 13
32 Size groups by kind | Size groups by kind | kind, groups, share of groups, cumulative share | 13
33 Size groups by kind | Size groups by kind | kind, piping, ventilation, heating_and_cooling, elements | 13
34 Elements by IFC class | Elements by IFC class | IFC class, elements, share of elements, cumulative share | 6
35 Elements by size method | Elements by size method | size method, elements, share of elements, cumulative share | 7
36 Elements by family | Elements by family | family, elements, share of elements, cumulative share | 14
37 Elements by cross-section sh | Elements by cross-section shape | shape, elements, share of elements, cumulative share | 3
38 Missing material, insulation | Missing material, insulation and predefined type | model, groups, groups with no material, groups with no insulation, groups with no predefined type, elements with no material | 3
39 System assignments | System assignments | model, system object type, assignments, share of that model's assignments, elements in the model, assignments minus elements | 9
40 Pipe segments by outside dia | Pipe segments by outside diameter | model, OD mm, segments, share of segments, length m, share of pipe length, cumulative length share, mean length per segment m, match status, clamps, articles | 9
41 Pipe-segment diameter statis | Pipe-segment diameter statistics | model, segments, length m, mean length per segment m, min OD mm, max OD mm, count-weighted mean OD mm, count-weighted median OD mm, count-weighted sample stdev mm, length-weighted mean OD mm, length-weighted median OD mm | 3
42 Pipe-segment diameter statis | Pipe-segment diameter statistics | series, n, sum, min, max, range, mean, median, sample stdev, q1, q3 | 1
43 Duct segments by cross-secti | Duct segments by cross-section | model, shape, size, width mm, height mm, OD mm, section area mm2, segments, length m, share of duct length, cumulative length share, mean length per segment m, match status, primary products | 5
44 Duct segments by cross-secti | Duct segments by cross-section | series, n, sum, min, max, range, mean, median, sample stdev, q1, q3 | 4
45 Devices and other bounding b | Devices and other bounding boxes | model, kind, IFC class, size, elements, share of all elements, bbox axis 1 mm, bbox axis 2 mm, bbox axis 3 mm, status, gap | 11
46 Coverage by kind | Coverage by kind | kind, groups, elements, matched elements, matched share, assumption elements, assumption share, unmatched elements, unmatched share | 13
47 Unmatched size groups | Unmatched size groups | model, kind, size, elements, share of that model, share of all elements, gap | 13
48 Primary-product utilisation | Primary-product utilisation | id, manufacturer, article, element type, groups, element hits, share of all elements | 18
49 Primary-product utilisation | Primary-product utilisation | series, n, sum, min, max, range, mean, median, sample stdev, q1, q3 | 1
50 Companion products under two | Companion products under two substrates | id, element type, threads, groups, substrate none, elements, substrate none, groups, substrate concrete, elements, substrate concrete | 5
51 Size-group census | Size-group census | model, kind, family, IFC class, size, elements, length m, size method, shape, status, primary products, assumption notes | 98
52 Architecture storeys | Architecture storeys | name, elevation m | 4
53 Architecture storeys | Architecture storeys | series, n, sum, min, max, range, mean, median, sample stdev, q1, q3 | 1
54 Architecture slabs and roofs | Architecture slabs and roofs | type, predefined type, thickness mm, z min m, z max m, count | 8
55 Architecture slabs and roofs | Architecture slabs and roofs | series, n, sum, min, max, range, mean, median, sample stdev, q1, q3 | 2
56 Architecture ceilings | Architecture ceilings | type, predefined type, thickness mm, z min m, z max m, count | 2
57 Architecture ceilings | Architecture ceilings | series, n, sum, min, max, range, mean, median, sample stdev, q1, q3 | 2
58 Architecture beams | Architecture beams | type, predefined type, thickness mm, z min m, z max m, count | 3
59 Architecture beams | Architecture beams | series, n, sum, min, max, range, mean, median, sample stdev, q1, q3 | 2
60 Ceiling to structure gaps | Ceiling to structure gaps | ceiling z max m, ceiling thickness mm, overhead, overhead z min m, gap mm, ceilings | 2
61 Ceiling to structure gaps | Ceiling to structure gaps | series, n, sum, min, max, range, mean, median, sample stdev, q1, q3 | 2
62 Sources | Sources | series, n, sum, min, max, range, mean, median, sample stdev, q1, q3 | 1
63 Sources | Sources | accessed, citations, share of citations, cumulative share | 1
64 Sources | Sources | source host, citations, share of citations, cumulative share | 19
65 Sources | Sources | title, url, citations, host | 24
66 Assumptions stored on produc | Assumptions stored on products | id, assumption | 3

## Narrative
Mounting-element statistics
Generated 30 October 2026, 08:04 CET from data/mounting_elements/products.json (schema version 1) and data/inventory/zenodo_duplex_mountable.json. Dataset: DuplexModel+MEP (Teclaw, Wojciech, 2024), DOI 10.5281/zenodo.10610773, CC BY 4.0.
Figures are counts, shares and descriptive statistics of fields that are actually stored. A null load, spacing or material stays empty. An element can match more than one clamp, so product-hit totals are not a partition of the element count. A system assignment total can exceed the element count when one element sits in more than one system. Coverage below uses substrate none, so concrete anchors are not counted as matches. The architecture ceilings are gypsum under timber joists.
Headline figures
Products by manufacturer
Each product counts once. Share is the share of the catalogue, not of the building.
Products by product line
Products by element type
duct_flex is listed even when the count is zero: the catalogue has no flex-duct hanger. A product with several element types would be counted in each column of the cross table and once in this table per type.
Manufacturer by element type
Products by role
Field completeness
Filled means the JSON value is not null and, for a list, not empty. max_support_spacing is null on every product: published spacing lives in guidance.
Article numbers: 23 stored, 23 distinct. Product ids: 23 stored, 23 distinct.
Connection threads
A clamp with M8/M10 is counted under both threads. The share is the share of catalogue products that include the thread, so the column can sum to more than 100%.
Products with an empty connection_threads list: 1 of 23.
Pipe-clamp windows
Span is max minus min of the published window. Load kN converts N by dividing by 1000 and leaves a cell empty when the source published no load. The definitions still differ by product and are not one allowable-load population.
Descriptive statistics of pipe-clamp windows
Overlapping pipe-clamp windows
Two windows overlap when their intervals meet within 0.02 mm, the same tolerance the mapper uses. A zero-width overlap is a shared boundary, so an outside diameter equal to that boundary matches both clamps.
Overlapping or boundary-touching pairs: 17.
Merged clamp coverage and holes
Depth is how many primary pipe clamps the mapper returns for each integer millimetre from the lowest published minimum to the highest published maximum.
Descriptive statistics of integer clamp depth
Clamp depth at each integer millimetre
Published loads
kN is the stored value when the unit is already kN, and the stored value divided by 1000 when the unit is N. Empty load cells are excluded from the descriptive rows. Kinds are kept apart because a recommended static load, a Nutzlast and an anchor Fzul are not interchangeable.
Products with no published load in the database: 10 of 23.
Anchors stored on products
Guidance records
Guidance rows: copper-tube-spacing-din1988-2-as-cited
Both catalogues print this as Richtwerte for copper and stainless tube and attribute it to DIN 1988 Teil 2. The standard text was not read for this database. The column copied here is straight length (Stangenrohr). The same IBP table gives shorter distances for copper coil (Ringrohr), for example 0.7–0.9 m at 15 mm, and those are not applied. No vertical-stack column is in this table. A row is offered for a modeled pipe only when the outside diameter is within 0.5 mm of a listed value, and only with the explicit assumption that the unnamed IFC material is the copper or stainless tube the table is about.
Guidance rows: lindab-duct-suspension-spacing
Swedish Lindab suspension guide, widely used for European spiral and rectangular duct. Vertical runs in the same section are limited to 3 m for both shapes. The size-table rows above are the uninsulated, no-fire-class case. Insulated and fire-rated tables in the same document are not copied.
Guidance rows: en-12236-duct-support-strength
DIN EN 12236:2002 (EN 12236:2002) specifies strength of supports for sheet-metal ductwork of any shape. It does not publish a spacing table. From the preview of the EN text: the fixing into the structure needs a safety factor of at least 3 on the calculated load; vertical members and the joint to the horizontal member need a safety factor of at least 1.5 against yield; horizontal-member deflection must not exceed 0.4 % of the distance between the vertical fixings. Fire loading is outside the standard's scope. No spacing number is derived from it here.
This record has no numeric rows.
Inventory by model
Elements by kind
Size groups by kind
Elements by IFC class
Elements by size method
Elements by family
Elements by cross-section shape
Missing material, insulation and predefined type
Counts are size groups. The inventory found no material name and no insulation on these models.
Size groups whose NominalDiameter property disagrees with the connected profile: 23 groups, 243 elements. Size groups with more than one outside diameter (reducers and similar): 17 groups, 132 elements.
System assignments
The count is the sum of system memberships stored on each size group. It can exceed the element count.
Pipe segments by outside diameter
Pipe-segment diameter statistics
Min, max, mean, median and sample stdev treat one segment as one observation, so a common small diameter pulls the mean down. The length-weighted columns weight each size by its recorded centreline length.
Duct segments by cross-section
Length-weighted mean rectangular width is 215.738 mm; height 180.336 mm; section area 41461.491 mm2.
Devices and other bounding boxes
Coverage by kind
Unmatched size groups
Unmatched groups: 13. Unmatched elements: 96 (8.3% of 1163).
Primary-product utilisation
Element hits sum the size groups for which the product is a primary match. A reducer that matches two clamps, and a diameter that matches three clamps, are counted once for each product. The shares can therefore sum to more than 100%.
Primary products with no hit in this inventory: none. Primary products with at least one hit: 18 of 18.
Companion products under two substrates
Companions are rods, channel and anchors returned with a primary match. substrate none is the duplex default. substrate concrete is the German commercial ceiling the anchor articles were recorded for. Each element is counted once per companion: a rod is attached when the matched clamps use that thread, and it is not multiplied by the number of clamps.
Size-group census
Architecture storeys
Architecture slabs and roofs
Architecture ceilings
Architecture beams
Ceiling to structure gaps
The floor and roof build-ups above the rooms use dimensional lumber and plywood, not a concrete soffit.
Ceilings are compound gypsum board on a metal-stud layer (57 mm in the material layer set), so a concrete ceiling anchor does not match this model's soffit.
Concrete in this architecture model is the slab on grade and the foundation walls, not the ceiling the MEP hangers would reach.
Sources
Distinct source URLs: 24. Citations counting a reused URL once per product or guidance record: 36.
Assumptions stored on products
Product assumption strings: 3 on 3 products.
IFC2X3 export: pipes and ducts are IfcFlowSegment, not IfcPipeSegment / IfcDuctSegment.
Segment property sets have length and roughness, not nominal diameter. Outside diameter is the circle-profile diameter.
Rectangular duct profiles mix run length into the profile. Width and height are the two edges that are not the port-to-port direction; height is the edge closer to world Z.
No insulation covering or insulation property was found on the MEP elements.
On fittings, NominalDiameter is an IfcPropertyListValue and often disagrees with the connected pipe's circle-profile diameter. Groups keep both; the profile diameter is the one a clamp has to fit.
Material entities on the MEP models are unnamed.

## 01 Headline figures
Headline figures
measure | value
products | 23
guidance records | 3
manufacturers | 6
primary products | 18
companion products | 5
inventory size groups | 98
inventory elements | 1163
elements matched on a published size | 777
elements matched with an assumption | 290
elements unmatched | 96
share matched on a published size | 66.8%
share matched with an assumption | 24.9%
share unmatched | 8.3%
pipe segment length, m | 303.832
duct segment length, m | 118.376
models | 3

## 02 Products by manufacturer
Products by manufacturer
manufacturer | products | share | primary | companion | with load | load empty | element types
Hilti | 6 | 26.1% | 3 | 3 | 3 | 3 | channel, pipe, threaded_rod
Kermi | 1 | 4.3% | 1 | 0 | 0 | 1 | radiator
Müpro | 3 | 13.0% | 3 | 0 | 0 | 3 | pipe
Sikla | 3 | 13.0% | 3 | 0 | 3 | 0 | duct_rectangular, duct_round
Walraven | 2 | 8.7% | 2 | 0 | 0 | 2 | pipe
fischer | 8 | 34.8% | 6 | 2 | 7 | 1 | ceiling_anchor, pipe

## 03 Products by product line
Products by product line
product line | manufacturer | products | share | roles | element types
FRS Plus | fischer | 4 | 17.4% | primary | pipe
MP-MI | Hilti | 3 | 13.0% | primary | pipe
OPTIMAL | Müpro | 3 | 13.0% | primary | pipe
AM | Hilti | 2 | 8.7% | companion | threaded_rod
EA II | fischer | 2 | 8.7% | companion | ceiling_anchor
LUW | Sikla | 2 | 8.7% | primary | duct_rectangular
BISMAT 2000 | Walraven | 1 | 4.3% | primary | pipe
BISMAT KSB 2 | Walraven | 1 | 4.3% | primary | pipe
FRS A2 | fischer | 1 | 4.3% | primary | pipe
FRS-L Universal | fischer | 1 | 4.3% | primary | pipe
MQ | Hilti | 1 | 4.3% | companion | channel
PLU 2G-N m.E. | Sikla | 1 | 4.3% | primary | duct_round
Wandkonsole variabel | Kermi | 1 | 4.3% | primary | radiator

## 04 Products by element type
Products by element type
element type | products | share of catalogue | primary | companion | with OD window | with nominal diameter | with load
pipe | 14 | 60.9% | 14 | 0 | 14 | 0 | 8
duct_round | 1 | 4.3% | 1 | 0 | 0 | 1 | 1
duct_rectangular | 2 | 8.7% | 2 | 0 | 0 | 0 | 2
duct_flex | 0 | 0.0% | 0 | 0 | 0 | 0 | 0
radiator | 1 | 4.3% | 1 | 0 | 0 | 0 | 0
threaded_rod | 2 | 8.7% | 0 | 2 | 0 | 0 | 0
channel | 1 | 4.3% | 0 | 1 | 0 | 0 | 0
ceiling_anchor | 2 | 8.7% | 0 | 2 | 0 | 0 | 2

## 05 Manufacturer by element type
Manufacturer by element type
manufacturer | pipe | duct_round | duct_rectangular | duct_flex | radiator | threaded_rod | channel | ceiling_anchor | products
Hilti | 3 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 6
Kermi | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
Müpro | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
Sikla | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 3
Walraven | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
fischer | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 8
all | 14 | 1 | 2 | 0 | 1 | 2 | 1 | 2 | 23

## 06 Products by role
Products by role
role | products | share | cumulative share
primary | 18 | 78.3% | 78.3%
companion | 5 | 21.7% | 100.0%

## 07 Field completeness
Field completeness
field | filled | empty | filled share
product_line | 23 | 0 | 100.0%
article_number | 23 | 0 | 100.0%
outer_diameter_mm | 14 | 9 | 60.9%
nominal_diameter_mm | 1 | 22 | 4.3%
connection_threads | 22 | 1 | 95.7%
load_rating | 13 | 10 | 56.5%
max_support_spacing | 0 | 23 | 0.0%
anchor | 3 | 20 | 13.0%
assumptions | 3 | 20 | 13.0%
notes | 23 | 0 | 100.0%
sources | 23 | 0 | 100.0%

## 08 Connection threads
Connection threads
thread | products | share of catalogue
M10 | 19 | 82.6%
M8 | 15 | 65.2%
M12 | 4 | 17.4%

## 09 Connection threads
Connection threads
thread combination | role | products | share of catalogue
(none) | primary | 1 | 4.3%
M10 | companion | 2 | 8.7%
M10 | primary | 1 | 4.3%
M10+M12 | primary | 3 | 13.0%
M12 | companion | 1 | 4.3%
M8 | companion | 2 | 8.7%
M8+M10 | primary | 13 | 56.5%

## 10 Pipe-clamp windows
Pipe-clamp windows
id | manufacturer | article | min mm | max mm | span mm | threads | load kN
fischer-frs-l-539443 | fischer | 539443 | 8 | 11 | 3 | M8, M10 | 0.7
fischer-frs-plus-079440 | fischer | 079440 | 12 | 15 | 3 | M8, M10 | 0.8
muepro-optimal-119866 | Müpro | 119866 | 13 | 15 | 2 | M8, M10
fischer-frs-plus-079441 | fischer | 079441 | 15 | 19 | 4 | M8, M10 | 0.8
hilti-mp-mi-20843 | Hilti | 20843 | 15 | 19 | 4 | M10, M12 | 1.8
muepro-optimal-119862 | Müpro | 119862 | 19 | 24 | 5 | M8, M10
fischer-frs-plus-079442 | fischer | 079442 | 20 | 24 | 4 | M8, M10 | 0.8
hilti-mp-mi-20845 | Hilti | 20845 | 20 | 25 | 5 | M10, M12 | 1.8
fischer-frs-plus-079445 | fischer | 079445 | 40 | 45 | 5 | M8, M10 | 1
hilti-mp-mi-20851 | Hilti | 20851 | 40 | 45 | 5 | M10, M12 | 1.8
muepro-optimal-119858 | Müpro | 119858 | 41 | 44 | 3 | M8, M10
walraven-bismat-2000-3403105 | Walraven | 3403105 | 100 | 105 | 5 | M8, M10
walraven-bismat-ksb2-3396105 | Walraven | 3396105 | 100 | 105 | 5 | M8, M10
fischer-frs-a2-064697 | fischer | 064697 | 102 | 116 | 14 | M10

## 11 Descriptive statistics of pi
Descriptive statistics of pipe-clamp windows
series | n | sum | min | max | range | mean | median | sample stdev | q1 | q3
window min, mm | 14 | 545 | 8 | 102 | 94 | 38.9286 | 20 | 35.1447 | 15 | 40.75
window max, mm | 14 | 612 | 11 | 116 | 105 | 43.7143 | 24.5 | 37.0123 | 19 | 45
window span, mm | 14 | 67 | 2 | 14 | 12 | 4.7857 | 4.5 | 2.8333 | 3.25 | 5
published load of these clamps, kN | 8 | 9.5 | 0.7 | 1.8 | 1.1 | 1.1875 | 0.9 | 0.51391 | 0.8 | 1.8

## 12 Overlapping pipe-clamp windo
Overlapping pipe-clamp windows
article A | article B | overlap min mm | overlap max mm | overlap width mm
119866 | 079440 | 13 | 15 | 2
079440 | 079441 | 15 | 15 | 0
079440 | 20843 | 15 | 15 | 0
079441 | 20843 | 15 | 19 | 4
119866 | 079441 | 15 | 15 | 0
119866 | 20843 | 15 | 15 | 0
119862 | 079441 | 19 | 19 | 0
119862 | 20843 | 19 | 19 | 0
079442 | 20845 | 20 | 24 | 4
119862 | 079442 | 20 | 24 | 4
119862 | 20845 | 20 | 24 | 4
079445 | 20851 | 40 | 45 | 5
119858 | 079445 | 41 | 44 | 3
119858 | 20851 | 41 | 44 | 3
3396105 | 3403105 | 100 | 105 | 5
064697 | 3396105 | 102 | 105 | 3
064697 | 3403105 | 102 | 105 | 3

## 13 Merged clamp coverage and ho
Merged clamp coverage and holes
covered from mm | covered to mm | width mm
8 | 11 | 3
12 | 25 | 13
40 | 45 | 5
100 | 116 | 16

## 14 Merged clamp coverage and ho
Merged clamp coverage and holes
hole after mm | hole before mm | width mm
11 | 12 | 1
25 | 40 | 15
45 | 100 | 55

## 15 Descriptive statistics of in
Descriptive statistics of integer clamp depth
series | n | sum | min | max | range | mean | median | sample stdev | q1 | q3
clamps covering each integer mm | 109 | 81 | 0 | 4 | 4 | 0.74312 | 0 | 1.1172 | 0 | 1

## 16 Descriptive statistics of in
Descriptive statistics of integer clamp depth
clamps at that mm | integer mm count | share of the scanned mm | cumulative share
0 | 68 | 62.4% | 62.4%
1 | 17 | 15.6% | 78.0%
3 | 14 | 12.8% | 90.8%
2 | 9 | 8.3% | 99.1%
4 | 1 | 0.9% | 100.0%

## 17 Descriptive statistics of in
Descriptive statistics of integer clamp depth
uncovered integers from mm | uncovered integers to mm | count of integers
26 | 39 | 14
46 | 99 | 54

## 18 Clamp depth at each integer
Clamp depth at each integer millimetre
mm | matching clamps | product ids
8 | 1 | fischer-frs-l-539443
9 | 1 | fischer-frs-l-539443
10 | 1 | fischer-frs-l-539443
11 | 1 | fischer-frs-l-539443
12 | 1 | fischer-frs-plus-079440
13 | 2 | muepro-optimal-119866, fischer-frs-plus-079440
14 | 2 | muepro-optimal-119866, fischer-frs-plus-079440
15 | 4 | muepro-optimal-119866, fischer-frs-plus-079440, fischer-frs-plus-079441, hilti-mp-mi-20843
16 | 2 | fischer-frs-plus-079441, hilti-mp-mi-20843
17 | 2 | fischer-frs-plus-079441, hilti-mp-mi-20843
18 | 2 | fischer-frs-plus-079441, hilti-mp-mi-20843
19 | 3 | muepro-optimal-119862, fischer-frs-plus-079441, hilti-mp-mi-20843
20 | 3 | muepro-optimal-119862, fischer-frs-plus-079442, hilti-mp-mi-20845
21 | 3 | muepro-optimal-119862, fischer-frs-plus-079442, hilti-mp-mi-20845
22 | 3 | muepro-optimal-119862, fischer-frs-plus-079442, hilti-mp-mi-20845
23 | 3 | muepro-optimal-119862, fischer-frs-plus-079442, hilti-mp-mi-20845
24 | 3 | muepro-optimal-119862, fischer-frs-plus-079442, hilti-mp-mi-20845
25 | 1 | hilti-mp-mi-20845
26 | 0
27 | 0
28 | 0
29 | 0
30 | 0
31 | 0
32 | 0
33 | 0
34 | 0
35 | 0
36 | 0
37 | 0
38 | 0
39 | 0
40 | 2 | fischer-frs-plus-079445, hilti-mp-mi-20851
41 | 3 | muepro-optimal-119858, fischer-frs-plus-079445, hilti-mp-mi-20851
42 | 3 | muepro-optimal-119858, fischer-frs-plus-079445, hilti-mp-mi-20851
43 | 3 | muepro-optimal-119858, fischer-frs-plus-079445, hilti-mp-mi-20851
44 | 3 | muepro-optimal-119858, fischer-frs-plus-079445, hilti-mp-mi-20851
45 | 2 | fischer-frs-plus-079445, hilti-mp-mi-20851
46 | 0
47 | 0
48 | 0
49 | 0
50 | 0
51 | 0
52 | 0
53 | 0
54 | 0
55 | 0
56 | 0
57 | 0
58 | 0
59 | 0
60 | 0
61 | 0
62 | 0
63 | 0
64 | 0
65 | 0
66 | 0
67 | 0
68 | 0
69 | 0
70 | 0
71 | 0
72 | 0
73 | 0
74 | 0
75 | 0
76 | 0
77 | 0
78 | 0
79 | 0
80 | 0
81 | 0
82 | 0
83 | 0
84 | 0
85 | 0
86 | 0
87 | 0
88 | 0
89 | 0
90 | 0
91 | 0
92 | 0
93 | 0
94 | 0
95 | 0
96 | 0
97 | 0
98 | 0
99 | 0
100 | 2 | walraven-bismat-ksb2-3396105, walraven-bismat-2000-3403105
101 | 2 | walraven-bismat-ksb2-3396105, walraven-bismat-2000-3403105
102 | 3 | fischer-frs-a2-064697, walraven-bismat-ksb2-3396105, walraven-bismat-2000-3403105
103 | 3 | fischer-frs-a2-064697, walraven-bismat-ksb2-3396105, walraven-bismat-2000-3403105
104 | 3 | fischer-frs-a2-064697, walraven-bismat-ksb2-3396105, walraven-bismat-2000-3403105
105 | 3 | fischer-frs-a2-064697, walraven-bismat-ksb2-3396105, walraven-bismat-2000-3403105
106 | 1 | fischer-frs-a2-064697
107 | 1 | fischer-frs-a2-064697
108 | 1 | fischer-frs-a2-064697
109 | 1 | fischer-frs-a2-064697
110 | 1 | fischer-frs-a2-064697
111 | 1 | fischer-frs-a2-064697
112 | 1 | fischer-frs-a2-064697
113 | 1 | fischer-frs-a2-064697
114 | 1 | fischer-frs-a2-064697
115 | 1 | fischer-frs-a2-064697
116 | 1 | fischer-frs-a2-064697

## 19 Published loads
Published loads
id | manufacturer | element type | value | unit | kN | kind
fischer-frs-l-539443 | fischer | pipe | 0.7 | kN | 0.7 | max. recommended static load, centric tension
fischer-frs-plus-079440 | fischer | pipe | 0.8 | kN | 0.8 | max. recommended static load, centric tension
fischer-frs-plus-079441 | fischer | pipe | 0.8 | kN | 0.8 | max. recommended static load, centric tension
fischer-frs-plus-079442 | fischer | pipe | 0.8 | kN | 0.8 | max. recommended static load, centric tension
fischer-frs-plus-079445 | fischer | pipe | 1 | kN | 1 | max. recommended static load, centric tension
hilti-mp-mi-20843 | Hilti | pipe | 1800 | N | 1.8 | maximum load F, ambient, for the 15–64 mm band of MP-MI series G
hilti-mp-mi-20845 | Hilti | pipe | 1800 | N | 1.8 | maximum load F, ambient, for the 15–64 mm band of MP-MI series G
hilti-mp-mi-20851 | Hilti | pipe | 1800 | N | 1.8 | maximum load F, ambient, for the 15–64 mm band of MP-MI series G
sikla-plu-2g-199893 | Sikla | duct_round | 0.8 | kN | 0.8 | zulässige Nutzlast for types 71–200
sikla-luw-sl-189893 | Sikla | duct_rectangular | 0.8 | kN | 0.8 | Nennlast
sikla-luw-sz-189902 | Sikla | duct_rectangular | 0.8 | kN | 0.8 | Nennlast
fischer-ea-ii-m8-532231 | fischer | ceiling_anchor | 1.4 | kN | 1.4 | permissible load Fzul of one anchor for redundant non-structural use in concrete C20/25 to C50/60
fischer-ea-ii-m10-532232 | fischer | ceiling_anchor | 1.9 | kN | 1.9 | permissible load Fzul of one anchor for redundant non-structural use in concrete C20/25 to C50/60

## 20 Published loads
Published loads
series | n | sum | min | max | range | mean | median | sample stdev | q1 | q3
all published loads converted to kN | 13 | 15.2 | 0.7 | 1.9 | 1.2 | 1.1692 | 0.8 | 0.48714 | 0.8 | 1.8
Nennlast | 2 | 1.6 | 0.8 | 0.8 | 0 | 0.8 | 0.8 | 0
max. recommended static load, centric tension | 5 | 4.1 | 0.7 | 1 | 0.3 | 0.82 | 0.8 | 0.10954 | 0.8 | 0.8
maximum load F, ambient, for the 15–64 mm band of MP-MI series G | 3 | 5.4 | 1.8 | 1.8 | 0 | 1.8 | 1.8 | 0
permissible load Fzul of one anchor for redundant non-structural use in concrete C20/25 to C50/60 | 2 | 3.3 | 1.4 | 1.9 | 0.5 | 1.65 | 1.65 | 0.35355
zulässige Nutzlast for types 71–200 | 1 | 0.8 | 0.8 | 0.8 | 0 | 0.8 | 0.8

## 21 Published loads
Published loads
id | manufacturer | element type | article
muepro-optimal-119866 | Müpro | pipe | 119866
muepro-optimal-119862 | Müpro | pipe | 119862
muepro-optimal-119858 | Müpro | pipe | 119858
fischer-frs-a2-064697 | fischer | pipe | 064697
walraven-bismat-ksb2-3396105 | Walraven | pipe | 3396105
walraven-bismat-2000-3403105 | Walraven | pipe | 3403105
hilti-mq-41-3-369596 | Hilti | channel | 369596
hilti-rod-am8-339793 | Hilti | threaded_rod | 339793
hilti-rod-am10-339795 | Hilti | threaded_rod | 339795
kermi-console-zb02870003 | Kermi | radiator | ZB02870003

## 22 Anchors stored on products
Anchors stored on products
id | manufacturer | anchor type | thread | substrate | included fixings | load kN
fischer-ea-ii-m8-532231 | fischer | hammer-set internally threaded anchor | M8 | concrete | None | 1.4
fischer-ea-ii-m10-532232 | fischer | hammer-set internally threaded anchor | M10 | concrete | None | 1.9
kermi-console-zb02870003 | Kermi | wall plug and screw, included with the console set | None | wall | 2 screws 8×60 mm, 2 plugs 10×60 mm, 2 washers

## 23 Anchors stored on products
Anchors stored on products
substrate | products | share of anchored products | cumulative share
concrete | 2 | 66.7% | 66.7%
wall | 1 | 33.3% | 100.0%

## 24 Guidance records
Guidance records
id | applies to | rows | rows flagged table_row | sources | note characters
copper-tube-spacing-din1988-2-as-cited | pipe | 12 |  | 2 | 610
lindab-duct-suspension-spacing | duct_round, duct_rectangular | 6 | 4 | 1 | 292
en-12236-duct-support-strength | duct_round, duct_rectangular, duct_flex | 0 |  | 2 | 557

## 25 Guidance rows copper-tube-sp
Guidance rows: copper-tube-spacing-din1988-2-as-cited
outer_diameter_mm | horizontal_m | form
12 | 1.25 | stangenrohr
15 | 1.25 | stangenrohr
18 | 1.5 | stangenrohr
22 | 2 | stangenrohr
28 | 2.25 | stangenrohr
35 | 2.75 | stangenrohr
42 | 3 | stangenrohr
54 | 3.5 | stangenrohr
64 | 4 | stangenrohr
76.1 | 4.25 | stangenrohr
88.9 | 4.75 | stangenrohr
108 | 5 | stangenrohr

## 26 Guidance rows copper-tube-sp
Guidance rows: copper-tube-spacing-din1988-2-as-cited
series | n | sum | min | max | range | mean | median | sample stdev | q1 | q3
horizontal spacing, m | 12 | 35.5 | 1.25 | 5 | 3.75 | 2.9583 | 2.875 | 1.3435 | 1.875 | 4.0625

## 27 Guidance rows copper-tube-sp
Guidance rows: copper-tube-spacing-din1988-2-as-cited
series | n | sum | min | max | range | mean | median | sample stdev | q1 | q3
table outside diameter, mm | 12 | 563 | 12 | 108 | 96 | 46.9167 | 38.5 | 31.4879 | 21 | 67.025

## 28 Guidance rows lindab-duct-su
Guidance rows: lindab-duct-suspension-spacing
shape | diameter_mm | horizontal_m | table_row | conditions | width_mm | height_mm
round | 150 | 3 | yes | uninsulated circular duct, no fire class; recommended spacing 3.0 m across the listed hanger types
rectangular |  | 2.4 | yes | uninsulated rectangular duct, no fire class | 200 | 150
rectangular |  | 2.4 | yes | uninsulated rectangular duct, no fire class | 300 | 150
rectangular |  | 2.4 | yes | uninsulated rectangular duct, no fire class | 300 | 300
rectangular |  | 2.4 | no | stated maximum hanger spacing for horizontal rectangular duct in that section, because more than one duct joint between hangers is considered unsuitable. 150×150 mm is not a row in the size table, which starts at width 200 mm. | None | None
round | None | 3 | no | stated maximum hanger spacing for horizontal circular duct in that section

## 29 Guidance rows lindab-duct-su
Guidance rows: lindab-duct-suspension-spacing
series | n | sum | min | max | range | mean | median | sample stdev | q1 | q3
horizontal spacing of table_row true, m | 4 | 10.2 | 2.4 | 3 | 0.6 | 2.55 | 2.4 | 0.3 | 2.4 | 2.55

## 30 Inventory by model
Inventory by model
model | file | schema | elements | share of elements | groups | recorded length m | elements matched | elements with assumption | elements unmatched | element matched share | element unmatched share | groups matched | groups with assumption | groups unmatched
piping | zenodo-duplex-piping.ifc | IFC2X3 | 463 | 39.8% | 41 | 108.565 | 449 | 0 | 14 | 97.0% | 3.0% | 37 | 0 | 4
ventilation | zenodo-duplex-ventilation.ifc | IFC2X3 | 374 | 32.2% | 40 | 118.376 | 20 | 274 | 80 | 5.3% | 21.4% | 3 | 29 | 8
heating_and_cooling | HeatingAndCooling.ifc | IFC2X3 | 326 | 28.0% | 17 | 195.267 | 308 | 16 | 2 | 94.5% | 0.6% | 15 | 1 | 1

## 31 Elements by kind
Elements by kind
kind | elements | share of elements | cumulative share
pipe_fitting | 386 | 33.2% | 33.2%
pipe_segment | 357 | 30.7% | 63.9%
duct_fitting | 156 | 13.4% | 77.3%
duct_segment | 126 | 10.8% | 88.1%
air_terminal | 40 | 3.4% | 91.6%
duct_flex | 36 | 3.1% | 94.7%
radiator | 16 | 1.4% | 96.0%
pipe_accessory | 14 | 1.2% | 97.2%
duct_accessory | 14 | 1.2% | 98.5%
sanitary_fixture | 12 | 1.0% | 99.5%
water_heater | 2 | 0.2% | 99.7%
air_handling_unit | 2 | 0.2% | 99.8%
stove | 2 | 0.2% | 100.0%

## 32 Size groups by kind
Size groups by kind
kind | groups | share of groups | cumulative share
pipe_fitting | 40 | 40.8% | 40.8%
duct_fitting | 25 | 25.5% | 66.3%
pipe_segment | 9 | 9.2% | 75.5%
duct_segment | 5 | 5.1% | 80.6%
air_terminal | 4 | 4.1% | 84.7%
pipe_accessory | 3 | 3.1% | 87.8%
sanitary_fixture | 3 | 3.1% | 90.8%
duct_accessory | 3 | 3.1% | 93.9%
duct_flex | 2 | 2.0% | 95.9%
water_heater | 1 | 1.0% | 96.9%
air_handling_unit | 1 | 1.0% | 98.0%
radiator | 1 | 1.0% | 99.0%
stove | 1 | 1.0% | 100.0%

## 33 Size groups by kind
Size groups by kind
kind | piping | ventilation | heating_and_cooling | elements
air_handling_unit | 0 | 2 | 0 | 2
air_terminal | 0 | 40 | 0 | 40
duct_accessory | 0 | 14 | 0 | 14
duct_fitting | 0 | 156 | 0 | 156
duct_flex | 0 | 36 | 0 | 36
duct_segment | 0 | 126 | 0 | 126
pipe_accessory | 10 | 0 | 4 | 14
pipe_fitting | 233 | 0 | 153 | 386
pipe_segment | 206 | 0 | 151 | 357
radiator | 0 | 0 | 16 | 16
sanitary_fixture | 12 | 0 | 0 | 12
stove | 0 | 0 | 2 | 2
water_heater | 2 | 0 | 0 | 2

## 34 Elements by IFC class
Elements by IFC class
IFC class | elements | share of elements | cumulative share
IfcFlowFitting | 526 | 45.2% | 45.2%
IfcFlowSegment | 519 | 44.6% | 89.9%
IfcFlowTerminal | 84 | 7.2% | 97.1%
IfcFlowController | 28 | 2.4% | 99.5%
IfcBuildingElementProxy | 4 | 0.3% | 99.8%
IfcEnergyConversionDevice | 2 | 0.2% | 100.0%

## 35 Elements by size method
Elements by size method
size method | elements | share of elements | cumulative share
connected_segment_profile | 400 | 34.4% | 34.4%
circle_profile | 367 | 31.6% | 66.0%
connected_duct_segment | 168 | 14.4% | 80.4%
port_axis_against_extrusion | 116 | 10.0% | 90.4%
world_bbox | 74 | 6.4% | 96.7%
faceted_bbox_minor_axis | 20 | 1.7% | 98.5%
unresolved | 18 | 1.5% | 100.0%

## 36 Elements by family
Elements by family
family | elements | share of elements | cumulative share
(none) | 399 | 34.3% | 34.3%
elbow | 229 | 19.7% | 54.0%
transition | 209 | 18.0% | 72.0%
rectangular | 116 | 10.0% | 81.9%
tee | 88 | 7.6% | 89.5%
round_flex | 36 | 3.1% | 92.6%
supply | 20 | 1.7% | 94.3%
return | 18 | 1.5% | 95.9%
panel | 16 | 1.4% | 97.2%
volume_damper | 14 | 1.2% | 98.5%
round | 10 | 0.9% | 99.3%
cross | 4 | 0.3% | 99.7%
cap | 2 | 0.2% | 99.8%
exhaust | 2 | 0.2% | 100.0%

## 37 Elements by cross-section sh
Elements by cross-section shape
shape | elements | share of elements | cumulative share
(none) | 644 | 55.4% | 55.4%
round | 403 | 34.7% | 90.0%
rectangular | 116 | 10.0% | 100.0%

## 38 Missing material, insulation
Missing material, insulation and predefined type
model | groups | groups with no material | groups with no insulation | groups with no predefined type | elements with no material
piping | 41 | 41 | 41 | 41 | 463
ventilation | 40 | 40 | 40 | 40 | 374
heating_and_cooling | 17 | 17 | 17 | 17 | 326

## 39 System assignments
System assignments
model | system object type | assignments | share of that model's assignments | elements in the model | assignments minus elements
piping | Domestic Cold Water | 199 | 41.0% | 463 | 22
piping | Sanitary | 170 | 35.1% | 463 | 22
piping | Domestic Hot Water | 116 | 23.9% | 463 | 22
ventilation | Powietrze nawiewane | 188 | 49.3% | 374 | 7
ventilation | Powietrze recyrkulacyjne | 186 | 48.8% | 374 | 7
ventilation | Powietrze usuwane | 6 | 1.6% | 374 | 7
ventilation | Kanalizacja | 1 | 0.3% | 374 | 7
heating_and_cooling | Hydronic Return | 178 | 51.7% | 326 | 18
heating_and_cooling | Hydronic Supply | 166 | 48.3% | 326 | 18

## 40 Pipe segments by outside dia
Pipe segments by outside diameter
model | OD mm | segments | share of segments | length m | share of pipe length | cumulative length share | mean length per segment m | match status | clamps | articles
heating_and_cooling | 9.52 | 81 | 22.7% | 130.103 | 42.8% | 42.8% | 1.606 | matched | 1 | 539443
heating_and_cooling | 12.7 | 50 | 14.0% | 60.046 | 19.8% | 62.6% | 1.201 | matched | 1 | 079440
piping | 22.225 | 76 | 21.3% | 43.338 | 14.3% | 76.8% | 0.57 | matched | 3 | 119862, 079442, 20845
piping | 41.275 | 38 | 10.6% | 23.516 | 7.7% | 84.6% | 0.619 | matched | 3 | 119858, 079445, 20851
piping | 15.875 | 54 | 15.1% | 18.446 | 6.1% | 90.7% | 0.342 | matched | 2 | 079441, 20843
piping | 104.775 | 24 | 6.7% | 16.888 | 5.6% | 96.2% | 0.704 | matched | 3 | 064697, 3396105, 3403105
piping | 12.7 | 6 | 1.7% | 6.121 | 2.0% | 98.2% | 1.02 | matched | 1 | 079440
heating_and_cooling | 19.05 | 20 | 5.6% | 5.118 | 1.7% | 99.9% | 0.256 | matched | 1 | 119862
piping | 15 | 8 | 2.2% | 0.256 | 0.1% | 100.0% | 0.032 | matched | 4 | 119866, 079440, 079441, 20843

## 41 Pipe-segment diameter statis
Pipe-segment diameter statistics
model | segments | length m | mean length per segment m | min OD mm | max OD mm | count-weighted mean OD mm | count-weighted median OD mm | count-weighted sample stdev mm | length-weighted mean OD mm | length-weighted median OD mm
piping | 206 | 108.565 | 0.527 | 12.7 | 104.775 | 33.134 | 22.225 | 27.5825 | 37.5596 | 22.225
heating_and_cooling | 151 | 195.267 | 1.293 | 9.52 | 19.05 | 11.8352 | 9.52 | 3.1756 | 10.7477 | 9.52
all pipe segments | 357 | 303.832 | 0.851 | 9.52 | 104.775 | 24.1253 | 15.875 | 23.5239 | 20.3281 | 12.7

## 42 Pipe-segment diameter statis
Pipe-segment diameter statistics
series | n | sum | min | max | range | mean | median | sample stdev | q1 | q3
distinct pipe-segment OD values, one row per size group, mm | 9 | 253.12 | 9.52 | 104.775 | 95.255 | 28.1244 | 15.875 | 30.2276 | 12.7 | 22.225

## 43 Duct segments by cross-secti
Duct segments by cross-section
model | shape | size | width mm | height mm | OD mm | section area mm2 | segments | length m | share of duct length | cumulative length share | mean length per segment m | match status | primary products
ventilation | rectangular | 200.0 × 150.0 mm | 200 | 150 | None | 30000 | 46 | 43.655 | 36.9% | 36.9% | 0.949 | matched_with_assumption | 2
ventilation | rectangular | 150.0 × 150.0 mm | 150 | 150 | None | 22500 | 30 | 31.835 | 26.9% | 63.8% | 1.061 | matched_with_assumption | 2
ventilation | rectangular | 300.0 × 300.0 mm | 300 | 300 | None | 90000 | 22 | 21.939 | 18.5% | 82.3% | 0.997 | matched_with_assumption | 2
ventilation | rectangular | 300.0 × 150.0 mm | 300 | 150 | None | 45000 | 18 | 11.051 | 9.3% | 91.6% | 0.614 | matched_with_assumption | 2
ventilation | round | OD 150.0 mm | None | None | 150 |  | 10 | 9.896 | 8.4% | 100.0% | 0.99 | matched | 1

## 44 Duct segments by cross-secti
Duct segments by cross-section
series | n | sum | min | max | range | mean | median | sample stdev | q1 | q3
rectangular duct width, one size group, mm | 4 | 950 | 150 | 300 | 150 | 237.5 | 250 | 75 | 187.5 | 300
rectangular duct height, one size group, mm | 4 | 750 | 150 | 300 | 150 | 187.5 | 150 | 75 | 150 | 187.5
rectangular section area, one size group, mm2 | 4 | 187500 | 22500 | 90000 | 67500 | 46875 | 37500 | 30233.4666 | 28125 | 56250
duct segment length, one size group, m | 5 | 118.376 | 9.896 | 43.655 | 33.759 | 23.6752 | 21.939 | 14.3006 | 11.051 | 31.835

## 45 Devices and other bounding b
Devices and other bounding boxes
model | kind | IFC class | size | elements | share of all elements | bbox axis 1 mm | bbox axis 2 mm | bbox axis 3 mm | status | gap
piping | sanitary_fixture | IfcFlowTerminal | bbox 228.2 × 510 × 635 mm | 4 | 0.3% | 228.2 | 510 | 635 | unmatched | No sanitary carrier or fixture bracket is in the database.
piping | sanitary_fixture | IfcFlowTerminal | bbox 361.9 × 584.3 × 722.5 mm | 4 | 0.3% | 361.9 | 584.3 | 722.5 | unmatched | No sanitary carrier or fixture bracket is in the database.
piping | sanitary_fixture | IfcFlowTerminal | bbox 457 × 457.2 × 485.8 mm | 4 | 0.3% | 457 | 457.2 | 485.8 | unmatched | No sanitary carrier or fixture bracket is in the database.
piping | water_heater | IfcBuildingElementProxy | bbox 350 × 500 × 1000 mm | 2 | 0.2% | 350 | 500 | 1000 | unmatched | No water-heater support is in the database. The proxy is a floor-standing appliance, not a suspended pipe.
ventilation | air_handling_unit | IfcBuildingElementProxy | bbox 475 × 1100 × 1400 mm | 2 | 0.2% | 475 | 1100 | 1400 | unmatched | No air-handling-unit frame is in the database.
ventilation | air_terminal | IfcFlowTerminal | bbox 101.6 × 200 × 200 mm | 18 | 1.5% | 101.6 | 200 | 200 | unmatched | No diffuser or grille fixing is in the database.
ventilation | air_terminal | IfcFlowTerminal | bbox 101.6 × 200 × 200 mm | 18 | 1.5% | 101.6 | 200 | 200 | unmatched | No diffuser or grille fixing is in the database.
ventilation | air_terminal | IfcFlowTerminal | bbox 40 × 300 × 300 mm | 2 | 0.2% | 40 | 300 | 300 | unmatched | No diffuser or grille fixing is in the database.
ventilation | air_terminal | IfcFlowTerminal | bbox 40 × 300 × 300 mm | 2 | 0.2% | 40 | 300 | 300 | unmatched | No diffuser or grille fixing is in the database.
heating_and_cooling | radiator | IfcFlowTerminal | bbox 100 × 350 × 1000 mm | 16 | 1.4% | 100 | 350 | 1000 | matched_with_assumption
heating_and_cooling | stove | IfcEnergyConversionDevice | bbox 350 × 500 × 1000 mm | 2 | 0.2% | 350 | 500 | 1000 | unmatched | No stove or boiler support is in the database. The element is floor-standing equipment.

## 46 Coverage by kind
Coverage by kind
kind | groups | elements | matched elements | matched share | assumption elements | assumption share | unmatched elements | unmatched share
air_handling_unit | 1 | 2 | 0 | 0.0% | 0 | 0.0% | 2 | 100.0%
air_terminal | 4 | 40 | 0 | 0.0% | 0 | 0.0% | 40 | 100.0%
duct_accessory | 3 | 14 | 0 | 0.0% | 14 | 100.0% | 0 | 0.0%
duct_fitting | 25 | 156 | 10 | 6.4% | 144 | 92.3% | 2 | 1.3%
duct_flex | 2 | 36 | 0 | 0.0% | 0 | 0.0% | 36 | 100.0%
duct_segment | 5 | 126 | 10 | 7.9% | 116 | 92.1% | 0 | 0.0%
pipe_accessory | 3 | 14 | 14 | 100.0% | 0 | 0.0% | 0 | 0.0%
pipe_fitting | 40 | 386 | 386 | 100.0% | 0 | 0.0% | 0 | 0.0%
pipe_segment | 9 | 357 | 357 | 100.0% | 0 | 0.0% | 0 | 0.0%
radiator | 1 | 16 | 0 | 0.0% | 16 | 100.0% | 0 | 0.0%
sanitary_fixture | 3 | 12 | 0 | 0.0% | 0 | 0.0% | 12 | 100.0%
stove | 1 | 2 | 0 | 0.0% | 0 | 0.0% | 2 | 100.0%
water_heater | 1 | 2 | 0 | 0.0% | 0 | 0.0% | 2 | 100.0%

## 47 Unmatched size groups
Unmatched size groups
model | kind | size | elements | share of that model | share of all elements | gap
piping | sanitary_fixture | bbox 228.2 × 510 × 635 mm | 4 | 0.9% | 0.3% | No sanitary carrier or fixture bracket is in the database.
piping | sanitary_fixture | bbox 361.9 × 584.3 × 722.5 mm | 4 | 0.9% | 0.3% | No sanitary carrier or fixture bracket is in the database.
piping | sanitary_fixture | bbox 457 × 457.2 × 485.8 mm | 4 | 0.9% | 0.3% | No sanitary carrier or fixture bracket is in the database.
piping | water_heater | bbox 350 × 500 × 1000 mm | 2 | 0.4% | 0.2% | No water-heater support is in the database. The proxy is a floor-standing appliance, not a suspended pipe.
ventilation | air_handling_unit | bbox 475 × 1100 × 1400 mm | 2 | 0.5% | 0.2% | No air-handling-unit frame is in the database.
ventilation | air_terminal | bbox 101.6 × 200 × 200 mm | 18 | 4.8% | 1.5% | No diffuser or grille fixing is in the database.
ventilation | air_terminal | bbox 101.6 × 200 × 200 mm | 18 | 4.8% | 1.5% | No diffuser or grille fixing is in the database.
ventilation | air_terminal | bbox 40 × 300 × 300 mm | 2 | 0.5% | 0.2% | No diffuser or grille fixing is in the database.
ventilation | air_terminal | bbox 40 × 300 × 300 mm | 2 | 0.5% | 0.2% | No diffuser or grille fixing is in the database.
ventilation | duct_fitting | connected duct unresolved | 2 | 0.5% | 0.2% | No connected duct size was recovered, so no duct hanger can be selected.
ventilation | duct_flex | mesh minor axis 151.6 mm | 20 | 5.3% | 1.7% | No product has a clamping range covering flex-duct mesh minor axis 151.6 mm. Sikla PLU type 150 is a spiral-seam clamp for nominal 150 mm and is not applied.
ventilation | duct_flex | diameter unresolved | 16 | 4.3% | 1.4% | Flex-duct diameter could not be recovered from the mesh, and no flex-duct hanger is in the database.
heating_and_cooling | stove | bbox 350 × 500 × 1000 mm | 2 | 0.6% | 0.2% | No stove or boiler support is in the database. The element is floor-standing equipment.

## 48 Primary-product utilisation
Primary-product utilisation
id | manufacturer | article | element type | groups | element hits | share of all elements
sikla-luw-sl-189893 | Sikla | 189893 | duct_rectangular | 29 | 274 | 23.6%
sikla-luw-sz-189902 | Sikla | 189902 | duct_rectangular | 29 | 274 | 23.6%
muepro-optimal-119862 | Müpro | 119862 | pipe | 18 | 252 | 21.7%
fischer-frs-plus-079442 | fischer | 079442 | pipe | 12 | 200 | 17.2%
hilti-mp-mi-20845 | Hilti | 20845 | pipe | 12 | 200 | 17.2%
fischer-frs-l-539443 | fischer | 539443 | pipe | 7 | 184 | 15.8%
fischer-frs-plus-079440 | fischer | 079440 | pipe | 16 | 174 | 15.0%
fischer-frs-plus-079441 | fischer | 079441 | pipe | 12 | 147 | 12.6%
hilti-mp-mi-20843 | Hilti | 20843 | pipe | 12 | 147 | 12.6%
fischer-frs-plus-079445 | fischer | 079445 | pipe | 10 | 84 | 7.2%
hilti-mp-mi-20851 | Hilti | 20851 | pipe | 10 | 84 | 7.2%
muepro-optimal-119858 | Müpro | 119858 | pipe | 10 | 84 | 7.2%
fischer-frs-a2-064697 | fischer | 064697 | pipe | 8 | 60 | 5.2%
walraven-bismat-2000-3403105 | Walraven | 3403105 | pipe | 8 | 60 | 5.2%
walraven-bismat-ksb2-3396105 | Walraven | 3396105 | pipe | 8 | 60 | 5.2%
sikla-plu-2g-199893 | Sikla | 199893 | duct_round | 7 | 34 | 2.9%
muepro-optimal-119866 | Müpro | 119866 | pipe | 3 | 20 | 1.7%
kermi-console-zb02870003 | Kermi | ZB02870003 | radiator | 1 | 16 | 1.4%

## 49 Primary-product utilisation
Primary-product utilisation
series | n | sum | min | max | range | mean | median | sample stdev | q1 | q3
element hits per primary product | 18 | 2354 | 16 | 274 | 258 | 130.7778 | 115.5 | 86.4105 | 60 | 196

## 50 Companion products under two
Companion products under two substrates
id | element type | threads | groups, substrate none | elements, substrate none | groups, substrate concrete | elements, substrate concrete
hilti-mq-41-3-369596 | channel | M12 | 29 | 274 | 29 | 274
hilti-rod-am8-339793 | threaded_rod | M8 | 84 | 1051 | 84 | 1051
hilti-rod-am10-339795 | threaded_rod | M10 | 84 | 1051 | 84 | 1051
fischer-ea-ii-m8-532231 | ceiling_anchor | M8 | 0 | 0 | 84 | 1051
fischer-ea-ii-m10-532232 | ceiling_anchor | M10 | 0 | 0 | 84 | 1051

## 51 Size-group census
Size-group census
model | kind | family | IFC class | size | elements | length m | size method | shape | status | primary products | assumption notes
piping | pipe_accessory | (none) | IfcFlowController | OD 22.225 mm | 8 |  | connected_segment_profile | (none) | matched | 3 | 0
piping | pipe_accessory | (none) | IfcFlowController | OD 15.875 mm | 2 |  | connected_segment_profile | (none) | matched | 2 | 0
piping | pipe_fitting | elbow | IfcFlowFitting | OD 22.225 mm | 38 |  | connected_segment_profile | (none) | matched | 3 | 1
piping | pipe_fitting | elbow | IfcFlowFitting | OD 15.875 mm | 34 |  | connected_segment_profile | (none) | matched | 2 | 1
piping | pipe_fitting | transition | IfcFlowFitting | OD 22.225 mm | 22 |  | connected_segment_profile | (none) | matched | 3 | 0
piping | pipe_fitting | elbow | IfcFlowFitting | OD 41.275 mm | 20 |  | connected_segment_profile | (none) | matched | 3 | 1
piping | pipe_fitting | transition | IfcFlowFitting | OD 15.875 / 22.225 mm | 18 |  | connected_segment_profile | (none) | matched | 5 | 0
piping | pipe_fitting | elbow | IfcFlowFitting | OD 104.775 mm | 12 |  | connected_segment_profile | (none) | matched | 3 | 1
piping | pipe_fitting | tee | IfcFlowFitting | OD 15.875 / 22.225 mm | 10 |  | connected_segment_profile | (none) | matched | 5 | 1
piping | pipe_fitting | transition | IfcFlowFitting | OD 22.225 / 104.775 mm | 10 |  | connected_segment_profile | (none) | matched | 6 | 0
piping | pipe_fitting | tee | IfcFlowFitting | OD 22.225 mm | 10 |  | connected_segment_profile | (none) | matched | 3 | 1
piping | pipe_fitting | transition | IfcFlowFitting | OD 15 / 15.875 mm | 8 |  | connected_segment_profile | (none) | matched | 4 | 0
piping | pipe_fitting | tee | IfcFlowFitting | OD 41.275 mm | 6 |  | connected_segment_profile | (none) | matched | 3 | 1
piping | pipe_fitting | transition | IfcFlowFitting | OD 15.875 mm | 5 |  | connected_segment_profile | (none) | matched | 2 | 0
piping | pipe_fitting | elbow | IfcFlowFitting | OD 12.7 mm | 4 |  | connected_segment_profile | (none) | matched | 1 | 0
piping | pipe_fitting | transition | IfcFlowFitting | OD 15 / 41.275 mm | 4 |  | connected_segment_profile | (none) | matched | 7 | 0
piping | pipe_fitting | tee | IfcFlowFitting | OD 41.275 / 104.775 mm | 4 |  | connected_segment_profile | (none) | matched | 6 | 1
piping | pipe_fitting | transition | IfcFlowFitting | OD 41.275 / 104.775 mm | 4 |  | connected_segment_profile | (none) | matched | 6 | 0
piping | pipe_fitting | tee | IfcFlowFitting | OD 104.775 mm | 2 |  | connected_segment_profile | (none) | matched | 3 | 1
piping | pipe_fitting | (none) | IfcFlowFitting | OD 104.775 mm | 2 |  | connected_segment_profile | (none) | matched | 3 | 1
piping | pipe_fitting | tee | IfcFlowFitting | OD 12.7 / 41.275 mm | 2 |  | connected_segment_profile | (none) | matched | 4 | 0
piping | pipe_fitting | transition | IfcFlowFitting | OD 12.7 / 41.275 mm | 2 |  | connected_segment_profile | (none) | matched | 4 | 0
piping | pipe_fitting | (none) | IfcFlowFitting | OD 12.7 mm | 2 |  | connected_segment_profile | (none) | matched | 1 | 1
piping | pipe_fitting | elbow | IfcFlowFitting | OD 15.875 / 22.225 mm | 2 |  | connected_segment_profile | (none) | matched | 5 | 1
piping | pipe_fitting | tee | IfcFlowFitting | OD 22.225 / 104.775 mm | 2 |  | connected_segment_profile | (none) | matched | 6 | 1
piping | pipe_fitting | (none) | IfcFlowFitting | OD 22.225 mm | 2 |  | connected_segment_profile | (none) | matched | 3 | 1
piping | pipe_fitting | (none) | IfcFlowFitting | OD 22.225 mm | 2 |  | connected_segment_profile | (none) | matched | 3 | 1
piping | pipe_fitting | transition | IfcFlowFitting | OD 41.275 mm | 2 |  | connected_segment_profile | (none) | matched | 3 | 0
piping | pipe_fitting | cap | IfcFlowTerminal | OD 41.275 mm | 2 |  | connected_segment_profile | (none) | matched | 3 | 0
piping | pipe_fitting | (none) | IfcFlowFitting | OD 15.875 mm | 1 |  | connected_segment_profile | (none) | matched | 2 | 1
piping | pipe_fitting | (none) | IfcFlowFitting | OD 15.875 mm | 1 |  | connected_segment_profile | (none) | matched | 2 | 1
piping | pipe_segment | (none) | IfcFlowSegment | OD 22.225 mm | 76 | 43.338 | circle_profile | round | matched | 3 | 1
piping | pipe_segment | (none) | IfcFlowSegment | OD 15.875 mm | 54 | 18.446 | circle_profile | round | matched | 2 | 1
piping | pipe_segment | (none) | IfcFlowSegment | OD 41.275 mm | 38 | 23.516 | circle_profile | round | matched | 3 | 1
piping | pipe_segment | (none) | IfcFlowSegment | OD 104.775 mm | 24 | 16.888 | circle_profile | round | matched | 3 | 1
piping | pipe_segment | (none) | IfcFlowSegment | OD 15.0 mm | 8 | 0.256 | circle_profile | round | matched | 4 | 1
piping | pipe_segment | (none) | IfcFlowSegment | OD 12.7 mm | 6 | 6.121 | circle_profile | round | matched | 1 | 1
piping | sanitary_fixture | (none) | IfcFlowTerminal | bbox 228.2 × 510 × 635 mm | 4 |  | world_bbox | (none) | unmatched | 0 | 0
piping | sanitary_fixture | (none) | IfcFlowTerminal | bbox 361.9 × 584.3 × 722.5 mm | 4 |  | world_bbox | (none) | unmatched | 0 | 0
piping | sanitary_fixture | (none) | IfcFlowTerminal | bbox 457 × 457.2 × 485.8 mm | 4 |  | world_bbox | (none) | unmatched | 0 | 0
piping | water_heater | (none) | IfcBuildingElementProxy | bbox 350 × 500 × 1000 mm | 2 |  | world_bbox | (none) | unmatched | 0 | 0
ventilation | air_handling_unit | (none) | IfcBuildingElementProxy | bbox 475 × 1100 × 1400 mm | 2 |  | world_bbox | (none) | unmatched | 0 | 0
ventilation | air_terminal | supply | IfcFlowTerminal | bbox 101.6 × 200 × 200 mm | 18 |  | world_bbox | (none) | unmatched | 0 | 0
ventilation | air_terminal | return | IfcFlowTerminal | bbox 101.6 × 200 × 200 mm | 18 |  | world_bbox | (none) | unmatched | 0 | 0
ventilation | air_terminal | exhaust | IfcFlowTerminal | bbox 40 × 300 × 300 mm | 2 |  | world_bbox | (none) | unmatched | 0 | 0
ventilation | air_terminal | supply | IfcFlowTerminal | bbox 40 × 300 × 300 mm | 2 |  | world_bbox | (none) | unmatched | 0 | 0
ventilation | duct_accessory | volume_damper | IfcFlowController | connected 200×150 mm | 6 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_accessory | volume_damper | IfcFlowController | connected 150×150 mm | 4 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_accessory | volume_damper | IfcFlowController | connected 300×150 mm | 4 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | transition | IfcFlowFitting | connected 200×150 mm | 28 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | transition | IfcFlowFitting | connected 150×150 mm | 26 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | elbow | IfcFlowFitting | connected 200×150 mm | 12 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | elbow | IfcFlowFitting | connected 150×150 mm | 10 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | elbow | IfcFlowFitting | connected 300×300 mm | 10 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | tee | IfcFlowFitting | connected 200×150 mm | 8 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | transition | IfcFlowFitting | connected Ø150 mm | 8 |  | connected_duct_segment | (none) | matched | 1 | 0
ventilation | duct_fitting | elbow | IfcFlowFitting | connected 300×150 mm | 6 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | transition | IfcFlowFitting | connected Ø150, 200×150 mm | 6 |  | connected_duct_segment | (none) | matched_with_assumption | 3 | 0
ventilation | duct_fitting | tee | IfcFlowFitting | connected 150×150 mm | 4 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | transition | IfcFlowFitting | connected 150×150, 300×300, 200×150 mm | 4 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | transition | IfcFlowFitting | connected 200×150, 300×300, 150×150 mm | 4 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | tee | IfcFlowFitting | connected 200×150, Ø150 mm | 4 |  | connected_duct_segment | (none) | matched_with_assumption | 3 | 0
ventilation | duct_fitting | transition | IfcFlowFitting | connected 300×150, 300×300 mm | 4 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | tee | IfcFlowFitting | connected 150×150, 200×150 mm | 2 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | tee | IfcFlowFitting | connected 150×150, 300×150 mm | 2 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | tee | IfcFlowFitting | connected 150×150, 300×150, 200×150 mm | 2 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | transition | IfcFlowFitting | connected 200×150, 150×150, 300×150 mm | 2 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | transition | IfcFlowFitting | connected 300×150, 200×150 mm | 2 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | tee | IfcFlowFitting | connected 300×150, Ø150 mm | 2 |  | connected_duct_segment | (none) | matched_with_assumption | 3 | 0
ventilation | duct_fitting | cross | IfcFlowFitting | connected 300×300, 150×150, 200×150 mm | 2 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | cross | IfcFlowFitting | connected 300×300, 200×150, 150×150 mm | 2 |  | connected_duct_segment | (none) | matched_with_assumption | 2 | 0
ventilation | duct_fitting | transition | IfcFlowFitting | connected duct unresolved | 2 |  | unresolved | (none) | unmatched | 0 | 0
ventilation | duct_fitting | elbow | IfcFlowFitting | connected Ø150 mm | 2 |  | connected_duct_segment | (none) | matched | 1 | 0
ventilation | duct_fitting | transition | IfcFlowFitting | connected Ø150, 300×150 mm | 2 |  | connected_duct_segment | (none) | matched_with_assumption | 3 | 0
ventilation | duct_flex | round_flex | IfcFlowSegment | mesh minor axis 151.6 mm | 20 |  | faceted_bbox_minor_axis | round | unmatched | 0 | 1
ventilation | duct_flex | round_flex | IfcFlowSegment | diameter unresolved | 16 |  | unresolved | round | unmatched | 0 | 1
ventilation | duct_segment | rectangular | IfcFlowSegment | 200.0 × 150.0 mm | 46 | 43.655 | port_axis_against_extrusion | rectangular | matched_with_assumption | 2 | 0
ventilation | duct_segment | rectangular | IfcFlowSegment | 150.0 × 150.0 mm | 30 | 31.835 | port_axis_against_extrusion | rectangular | matched_with_assumption | 2 | 0
ventilation | duct_segment | rectangular | IfcFlowSegment | 300.0 × 300.0 mm | 22 | 21.939 | port_axis_against_extrusion | rectangular | matched_with_assumption | 2 | 0
ventilation | duct_segment | rectangular | IfcFlowSegment | 300.0 × 150.0 mm | 18 | 11.051 | port_axis_against_extrusion | rectangular | matched_with_assumption | 2 | 0
ventilation | duct_segment | round | IfcFlowSegment | OD 150.0 mm | 10 | 9.896 | circle_profile | round | matched | 1 | 0
heating_and_cooling | pipe_accessory | (none) | IfcFlowController | OD 19.05 mm | 4 |  | connected_segment_profile | (none) | matched | 1 | 0
heating_and_cooling | pipe_fitting | elbow | IfcFlowFitting | OD 9.52 mm | 37 |  | connected_segment_profile | (none) | matched | 1 | 1
heating_and_cooling | pipe_fitting | transition | IfcFlowFitting | OD 9.52 / 12.7 mm | 30 |  | connected_segment_profile | (none) | matched | 2 | 0
heating_and_cooling | pipe_fitting | elbow | IfcFlowFitting | OD 12.7 mm | 22 |  | connected_segment_profile | (none) | matched | 1 | 1
heating_and_cooling | pipe_fitting | tee | IfcFlowFitting | OD 9.52 / 12.7 mm | 20 |  | connected_segment_profile | (none) | matched | 2 | 1
heating_and_cooling | pipe_fitting | elbow | IfcFlowTerminal | OD 9.52 mm | 12 |  | connected_segment_profile | (none) | matched | 1 | 0
heating_and_cooling | pipe_fitting | transition | IfcFlowFitting | OD 12.7 / 19.05 mm | 8 |  | connected_segment_profile | (none) | matched | 2 | 0
heating_and_cooling | pipe_fitting | transition | IfcFlowFitting | OD 19.05 mm | 8 |  | connected_segment_profile | (none) | matched | 1 | 0
heating_and_cooling | pipe_fitting | elbow | IfcFlowFitting | OD 19.05 mm | 8 |  | connected_segment_profile | (none) | matched | 1 | 1
heating_and_cooling | pipe_fitting | tee | IfcFlowFitting | OD 12.7 / 19.05 mm | 4 |  | connected_segment_profile | (none) | matched | 2 | 1
heating_and_cooling | pipe_fitting | tee | IfcFlowFitting | OD 9.52 / 12.7 mm | 2 |  | connected_segment_profile | (none) | matched | 2 | 1
heating_and_cooling | pipe_fitting | tee | IfcFlowTerminal | OD 9.52 / 12.7 mm | 2 |  | connected_segment_profile | (none) | matched | 2 | 0
heating_and_cooling | pipe_segment | (none) | IfcFlowSegment | OD 9.52 mm | 81 | 130.103 | circle_profile | round | matched | 1 | 1
heating_and_cooling | pipe_segment | (none) | IfcFlowSegment | OD 12.7 mm | 50 | 60.046 | circle_profile | round | matched | 1 | 1
heating_and_cooling | pipe_segment | (none) | IfcFlowSegment | OD 19.05 mm | 20 | 5.118 | circle_profile | round | matched | 1 | 1
heating_and_cooling | radiator | panel | IfcFlowTerminal | bbox 100 × 350 × 1000 mm | 16 |  | world_bbox | (none) | matched_with_assumption | 1 | 0
heating_and_cooling | stove | (none) | IfcEnergyConversionDevice | bbox 350 × 500 × 1000 mm | 2 |  | world_bbox | (none) | unmatched | 0 | 0

## 52 Architecture storeys
Architecture storeys
name | elevation m
T/FDN | -1.25
Level 1 | 0
Level 2 | 3.1
Roof | 6

## 53 Architecture storeys
Architecture storeys
series | n | sum | min | max | range | mean | median | sample stdev | q1 | q3
storey elevation, m | 4 | 7.85 | -1.25 | 6 | 7.25 | 1.9625 | 1.55 | 3.2541 | -0.3125 | 3.825

## 54 Architecture slabs and roofs
Architecture slabs and roofs
type | predefined type | thickness mm | z min m | z max m | count
Floor:127mm Slab on Grade | FLOOR | 127 | -0.127 | 0 | 2
Floor:Residential - Wood Joist with Subflooring | FLOOR | 305 | 2.795 | 3.1 | 2
Floor:Finish Floor - Wood | FLOOR | 19 | 3.1 | 3.119 | 6
Floor:Finish Floor - Ceramic Tile | FLOOR | 13 | 3.1 | 3.113 | 2
Floor:Finish Floor - Wood | FLOOR | 19 | 0 | 0.019 | 2
Floor:Finish Floor - Ceramic Tile | FLOOR | 13 | 0 | 0.013 | 4
Basic Roof:Live Roof over Wood Joist Flat Roof | ROOF | 457 | 6 | 6.457 | 1
Floor:150mm Exterior Slab on Grade | FLOOR | 150 | -0.137 | 0.013 | 2

## 55 Architecture slabs and roofs
Architecture slabs and roofs
series | n | sum | min | max | range | mean | median | sample stdev | q1 | q3
slabs thickness, one type row, mm | 8 | 1103 | 13 | 457 | 444 | 137.875 | 73 | 164.5283 | 17.5 | 188.75
slabs thickness, one instance, mm | 21 | 1851 | 13 | 457 | 444 | 88.1429 | 19 | 125.0813 | 13 | 127

## 56 Architecture ceilings
Architecture ceilings
type | predefined type | thickness mm | z min m | z max m | count
Compound Ceiling:Gypsum Board | CEILING | 57 | 2.5 | 2.557 | 4
Compound Ceiling:Gypsum Board | CEILING | 57 | 5.6 | 5.657 | 8

## 57 Architecture ceilings
Architecture ceilings
series | n | sum | min | max | range | mean | median | sample stdev | q1 | q3
ceilings thickness, one type row, mm | 2 | 114 | 57 | 57 | 0 | 57 | 57 | 0
ceilings thickness, one instance, mm | 12 | 684 | 57 | 57 | 0 | 57 | 57 | 0 | 57 | 57

## 58 Architecture beams
Architecture beams
type | predefined type | thickness mm | z min m | z max m | count
M_W-Wide Flange:W310X60 | (none) | 303 | 2.797 | 3.1 | 2
M_W-Wide Flange:W410X60 | (none) | 407 | 2.693 | 3.1 | 2
M_W-Wide Flange:W410X60 | (none) | 407 | 5.593 | 6 | 4

## 59 Architecture beams
Architecture beams
series | n | sum | min | max | range | mean | median | sample stdev | q1 | q3
beams thickness, one type row, mm | 3 | 1117 | 303 | 407 | 104 | 372.3333 | 407 | 60.0444
beams thickness, one instance, mm | 8 | 3048 | 303 | 407 | 104 | 381 | 407 | 48.1426 | 381 | 407

## 60 Ceiling to structure gaps
Ceiling to structure gaps
ceiling z max m | ceiling thickness mm | overhead | overhead z min m | gap mm | ceilings
2.557 | 57 | Floor:Residential - Wood Joist with Subflooring | 2.795 | 238 | 4
5.657 | 57 | Basic Roof:Live Roof over Wood Joist Flat Roof | 6 | 343 | 8

## 61 Ceiling to structure gaps
Ceiling to structure gaps
series | n | sum | min | max | range | mean | median | sample stdev | q1 | q3
clear gap, one ceiling instance, mm | 12 | 3696 | 238 | 343 | 105 | 308 | 343 | 51.6984 | 238 | 343
ceiling thickness in the gap table, one instance, mm | 12 | 684 | 57 | 57 | 0 | 57 | 57 | 0 | 57 | 57

## 62 Sources
Sources
series | n | sum | min | max | range | mean | median | sample stdev | q1 | q3
sources cited by one product | 23 | 31 | 1 | 2 | 1 | 1.3478 | 1 | 0.48698 | 1 | 2

## 63 Sources
Sources
accessed | citations | share of citations | cumulative share
2026-10-18 | 36 | 100.0% | 100.0%

## 64 Sources
Sources
source host | citations | share of citations | cumulative share
www.meinhausshop.de | 5 | 13.9% | 13.9%
www.dibt.de | 4 | 11.1% | 25.0%
www.muepro.de | 3 | 8.3% | 33.3%
1001krep.ru | 3 | 8.3% | 41.7%
www.sikla.de | 3 | 8.3% | 50.0%
heizung-billiger.de | 2 | 5.6% | 55.6%
assets.hilti.com | 2 | 5.6% | 61.1%
www.fischer.de | 2 | 5.6% | 66.7%
fiproductmedia.azureedge.net | 2 | 5.6% | 72.2%
www.fischer-international.com | 1 | 2.8% | 75.0%
www.unielektro.de | 1 | 2.8% | 77.8%
shop.famo24.de | 1 | 2.8% | 80.6%
www.sikla.ch | 1 | 2.8% | 83.3%
www.hilti.de | 1 | 2.8% | 86.1%
www.beijerref.de | 1 | 2.8% | 88.9%
storage.ua.prom.st | 1 | 2.8% | 91.7%
itsolution.lindab.com | 1 | 2.8% | 94.4%
cdn.standards.iteh.ai | 1 | 2.8% | 97.2%
doi.org | 1 | 2.8% | 100.0%

## 65 Sources
Sources
title | url | citations | host
fischer datasheet Rohrschelle FRS Plus | https://www.meinhausshop.de/media/pdf/94_046_22--DBL-01-de.pdf | 4 | www.meinhausshop.de
Distributor reproduction of the Hilti MP-MI load table | https://1001krep.ru/f/mp-mi.pdf | 3 | 1001krep.ru
ETA-18/0130 Hilti MP-MI pipe clamps | https://www.dibt.de/pdf_storage/2024/ETA-18!0130(8.06.02-122!21).pdf | 3 | www.dibt.de
Müpro OPTIMAL Rohrschelle article table | https://www.muepro.de/Produkte/Befestigungstechnik/Rohrschellen/OPTIMAL.html | 3 | www.muepro.de
fischer EA II permissible-load table | https://fiproductmedia.azureedge.net/media/Marketing%20Materials/Sales%20Materials/VKU_EAII_F_SDE_AIP_V2.pdf | 2 | fiproductmedia.azureedge.net
fischer SHK catalogue, Einschlaganker EA II article table | https://www.fischer.de/-/media/fixing-systems/rebrush/fide/service/infos-und-updates/informationsmaterial/documents/kataloge/katalog-sanitaer-v1.pdf | 2 | www.fischer.de
Sikla Lüftungswinkel LUW | https://www.sikla.de/startseite-131533/produkte-131535/e-katalog-131895/siconnect-3832/lueftung-10505/lueftungswinkel-luw-4160 | 2 | www.sikla.de
Hilti manual, medium-light installation systems, M8 threaded rod table | https://assets.hilti.com/api/public/content/5021068-original?v=Manuale+Sistemi+installazione+medio+leggere.pdf | 1 | assets.hilti.com
Hilti manual, medium-light installation systems, M10 threaded rod table | https://assets.hilti.com/api/public/content/5021068-original?v=Manuale+Sistemi+installazione+medio+leggere.pdf | 1 | assets.hilti.com
EN 12236:2002 preview (SIST EN 12236:2002) | https://cdn.standards.iteh.ai/samples/6392/f9a3d57c81574acb8ee255867c6daaca/SIST-EN-12236-2002.pdf | 1 | cdn.standards.iteh.ai
DIN EN 12236:2002-04 bibliographic record | https://doi.org/10.31030/9199301 | 1 | doi.org
Kermi Wandkonsolen-Set ZB02870003 reseller technical text | https://heizung-billiger.de/44039-kermi-wandkonsolen-set-variabel-mit-tiefenverstellung-wa-60-100-mm-weiss-kermi-zb02870003-4037486266503.html | 1 | heizung-billiger.de
Walraven BISMAT 2000 100–105 mm reseller listing (3403105) | https://heizung-billiger.de/727280-walraven-bismat-rohrschelle-2000-100-105mm-m8-m10-zweischraubenschelle-epdm-stahl-elektrolytisch-verzinkt-walraven-3403105-8712993004126.html | 1 | heizung-billiger.de
Lindab Ventilation, Upphängning av ventilationssystem | https://itsolution.lindab.com/lindabwebproductsdoc/pdf/documentation/ads/se/mounting/upphangning-ventsystem.pdf | 1 | itsolution.lindab.com
Walraven BIS KSB 2 100–105 mm reseller listing (Werksnummer 3396105) | https://shop.famo24.de/bis-zweischraubenschelle-ksb-2-100-105-mm-m8-10-ev-epdm/14810134 | 1 | shop.famo24.de
IBP technical catalogue, section 4.5 Befestigungsabstände | https://storage.ua.prom.st/657649_supersan_ibp_tk_all.pdf | 1 | storage.ua.prom.st
Conex installation notes, section 3.4 Befestigungsabstände | https://www.beijerref.de/media/ed/5c/fb/1758265815/conex-allgemeine-installationshinweise-ast-2241085.pdf | 1 | www.beijerref.de
ETA-18/0119 Hilti MQ installation channels | https://www.dibt.de/pdf_storage/2024/ETA-18!0119(8.06.02-121!21).pdf | 1 | www.dibt.de
fischer Pipe clamp FRS-L Universal | https://www.fischer-international.com/en/products/installation-systems/pipe-clamps/two-screw-pipe-clamps/pipe-clamp-frs-l-universal | 1 | www.fischer-international.com
Hilti MQ-41/3 product page | https://www.hilti.de/c/CLS_MODULAR_SUPPORT_SYSTEM/CLS_MODULAR_SUPPORT_PRO/r6130 | 1 | www.hilti.de
fischer datasheet Rohrschellen FRS A2/A4 | https://www.meinhausshop.de/media/pdf/meinhausshop-frs-a2-de.pdf | 1 | www.meinhausshop.de
Sikla Lüftungsschelle PLU 2G-N m.E. | https://www.sikla.ch/startseite-131533/produkte-131535/e-katalog-131895/siconnect-3832/lueftung-10505/lueftungsschelle-plu-2g-n-me-116704 | 1 | www.sikla.ch
Sikla Montagetechnik, Lüftungswinkel SZ note | https://www.sikla.de/fast/600/Montagetechnik_2023-04.pdf | 1 | www.sikla.de
Reseller listing FISCHER 539443 FRS-L Universal 8-11 | https://www.unielektro.de/FISCHER-539443-FRS-L-Universal-8-11-Rohrschelle--item-01253925 | 1 | www.unielektro.de

## 66 Assumptions stored on produc
Assumptions stored on products
id | assumption
sikla-luw-sl-189893 | The LUW datasheet describes suspension of rectangular ducts and does not publish a width or height window.
sikla-luw-sz-189902 | The LUW datasheet describes the SZ angle for a wide, low rectangular duct and does not publish a width or height window.
kermi-console-zb02870003 | The console is for Kermi radiators with hanging lugs 25 mm high and 2 mm thick. The duplex IFC radiator is named only Radiator and does not state a manufacturer or lugs.